## Sheet1
0 | 1 | 2
Customer:
End-user: |  | 29-01-19
Project
Site
Doc. no: |  | EL-18--0600 - Electric Motor
Revision:
Date:
By:
Item No. |  | P-6001 AB
Quantity |  | 2
Service |  | WIP
This requisition covers the specification of the design, the scope of supply, the applicable specifications and the commercial requirements for the supply of an horizontal squirrel cage induction motor. The supplier is responsible for quoting the most suitable equipment and raise questions when required. Any changes in the order stage will be for the account of the supplier. 1. DESIGN The design shall be in accordance with the applicable specifications and the following design criteria: Operational data
Electrical supply | V ph Hz | 11000 / 3 / 60
Hazardous Area (Zone,Group,Class) |  | Zone 2 Group IIA T3
Protection method motor |  | Eexd
JB material |  | Stainless Steel
Cooling medium driver |  | Air
Load data
Starting condition pump |  | DOL
Starting condition motor |  | Minimum flow
Inertia Total @ LS shaft | kgm2 | 1.35
Required torque open valve @ driver shaft | kNm | 3.16
Required torque min. flow @ driver shaft | kNm | 2.32
Required torque Shut-off @ driver shaft | kNm | 1.34
Motor data
Shaft type |  | Single
Rated driver power | kW | 1378
Rated driver speed | rpm | 3575
Driver lubrication |  | Self-contained
Lubricant capacity load motor @1.5barg | l/min | 4.7
Lubricant heat load motor | kW | 1.8
SPL limit motor (loaded) | dBA | 82
Quoted equipment shall be suitable for running to stand-still without external oil supply for example in case of power failure.