## Sheet1
0 | 1 | 2 | 3 | 4 | 5 | 6 | 7
Owner: CST-TD-EAD MTeemdpiluatme: M Vaoinl tDarigvees CPooncwepetr.v sDdistribution |  | Medium Voltage Power Distribution | Medium Voltage Power Distribution | Low Voltage Power Distribution
U [kV] 10 ± 5 % SCCMIN [MVA] | ??? * | U [kV] 10 ± 5 % SCCMIN [MVA] ??? * | U [kV] 10 ± 5 % S ??? *CCMIN [MVA] ??? * | U [V] 400 ± 5 % S CCMIN [MVA]
f [Hz] 50 ± 2 % Δ USTART [%] | ≤ 15 * | f [Hz] 50 ± 2 % SCCMAX [MVA] ??? * | f [Hz] 50 ± 2 % S ??? *CCMAX [MVA] ??? * | f [Hz] 50 ± 2 % S CCMAX [MVA]
| +B931.4 | +B932.4 |  | +B934.4
+B933.4
| Medium Voltage Switchgear | Medium Voltage Switchgear | Medium Voltage Switchgear
|  | MCB ON | MCB ON | Low Voltage Switchgear (MCC)
|  | OFF | OFF
|  | coils coilsUndervoltage release | Undervoltage release
+B931.3
| Auto - Transformer | +A932 |  | +A934
|  | Frequency Converter (VFD) | Frequency Converter (VFD)
Type Protection
| IP 42P [MVA] uk [%] | No. of pulses ** Protection | IP 42 No. of pulses | ** Protection
| forced airU [kV] 10 / 6 .. 7 Cooling | Cooling | forced air | Cooling
+A933
Frequency Converter (VFD)
|  |  |  | No. of pulses 6 |  | Protection | IP 42
Active Front End or
|  |  |  | forced airLine Harmonic Filter |  | Cooling
|  | ≤ 300m | ≤ 300m | ≤ 300m
+A931.5
Exciter Panel
Protection IP 42 | +A201 | +A205 |  | +A419 |  | +A420
Torque 0 .. 120 %
signal 4 .. 20 mA | Synchronous Motor | Asynchronous Motor with Squirrel Cage | Asynchronous Motor with Squirrel Cage | Asynchronous Motor with Squirrel Cage
P [kW] | 14000 Protection | IP 55 P [kW] 6000 Protection | IP 55 P [kW] 2350 | Protection IP 55 P [kW] | 300 | Protection | IP 55
U [kV] | 10 Ex Gas | Zone 2 I IB T3
MS |  | M U [kV] 6,6 Ex Gas | Zone 2 I IB T3 MU [kV] 6,6 | Ex Gas Zone 2 I IB T3 MU [V] | 400 | Ex Gas | Zone 2 I IB T3
3~ -1n [min | ] 1500,00 Ex Dust | Zone 22 I I IB T135°C 3~ nCT [min -1 ] 300 - 1500 Ex Dust | Zone 22 I I IB T135°C 3~ nCT [min -1 ] 180 - 1500 | Ex Dust Zone 22 I I IB T135°C 3~ nCT [min -1] | 600 - 1600 | Ex Dust | Zone 22 I I IB T135°C
-1
IS / IN | 3,5 + 0 tol. Cooling | IC81W air/water nCP [min -1 ] 1500 - 1800 Cooling | -1IC86W air/water nCP [min ] 1500 - 1800 | Cooling IC86W air/water nCP [min ] | N/A | Cooling | IC411 air surface
sleeveU S | / U N 0,6 .. 0,7 Bearings | forced oil lubricated Bearings | sleeve self oil lubricated | sleeveBearings self oil lubricated |  | Bearings | antifrictiongrease lubricated
| Extruder Main Drive |  | Melt Pump Drive | Pelletizer Drive
|  | ZSK 380 R356 | PR 100 - 9 | UG1250
Electrical equipment vendors | [6 empty] | Created Date Rev.
ABB Europe
ELIN Austria
GE Energy Europ2e
Hyosung Korea | Delivery and installation of LV and MV cables is not included in Coperion scope of supply, even if shown within scope limits.
Siemens Europe | MAIN DRIVES CONCEPTTotal harmonic distortion of variable speed drive systems according to IEEE 519 / GBT 14549-93.
TMEIC Japan |  |  | Buyer/Owner | Reference 32059316 |  |  | PAU 18.09.18 2
VEM Germany | * data to be confirmed by Buyer / Owner | IS / IN Starting current ratio | Coperion/Manufacturer |  |  |  | PAU 29.08.18 1
WEG Brazil | ** data to be confirmed by Manufacturer | US / UN Required starting voltage ratio at motor terminals |  | Project Toyo Irkutsk LL-HDPE |  |  | PAU 22.06.18 0